{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["监督检验报告信息"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"监督检验报告信息","index":0,"n_rows":8,"n_cols":12,"rows_kept":8,"cut":false,"hidden":false,"merged":[[0,0,0,11],[1,0,1,11]],"flags":["formulas_cached_only"]}
["附件1"]
["2024年消防水带产品质量市级监督抽查不合格情况汇总表"]
["序号","产品名称","抽查领域","企业名称","统一社会信用代码","标称生产企业名称","生产日期或批号","规格型号","商标","抽查结果","不合格项目","承检单位"]
[1,"有衬里消防水带","电商领域","济南市历城区冠超贸易商行（个体工商户）","92370112MADQ7PBT83","高邮市双龙消防设备有限公司","2024年4月/-","10-65-20-涤纶长丝/涤纶长丝-合成橡胶","扬龙","不合格","附着强度","山东省产品质量检验研究院"]
[2,"有衬里消防水带","流通领域","山东北斗消防科技有限公司","91370112MA3UG54498","山东北斗消防科技有限公司","2023年/-","8-65-25 涤纶长丝/涤纶长丝-聚氨酯","/","不合格","附着强度","山东省产品质量检验研究院"]
[3,"有衬里消防水带","流通领域","山东京高阀门有限公司","91370105MA3CAXJ5XT","泰州市泓源消防装备制造有限公司","2024年6月10日/-","8-65-25-涤纶长丝/涤纶长丝-合成橡胶","禾源","不合格","附着强度","山东省产品质量检验研究院"]
[4,"有衬里消防水带","电商领域","济南市历城区冠超贸易商行（个体工商户）","92370112MADQ7PBT83","高邮市双龙消防设备有限公司","2024年/-","8-65-20-涤纶长丝/涤纶长丝-合成橡胶","扬龙","不合格","附着强度","山东省产品质量检验研究院"]
[5,"有衬里消防水带","流通领域","天桥区万和消防器材经营部","92370105MA3F767X52","泰州威东消防科技有限公司","2023年11月/-","8-65-20-涤纶长丝/涤纶长丝-合成橡胶-A","/","不合格","附着强度；最小爆破压力","山东省产品质量检验研究院"]